## UPOWER
Number | Variable name | Program variable name | Function code(hex) | Address | Description | Unit | Times
Real-time data（read-only）0x3500-35FF
B1 | Grid charging input voltage | UP-ElectricChrgInVolt1 | 04（read） | 3500 | AC-DC Charging module - the AC input voltage | V | 100
B2 | Grid charging output voltage | UP-ElectricChrgOutVolt1 | 04（read） | 3505 | AC-DC Charging module - the DC output voltage | V | 100
B3 | Grid charging output current | UP-ElectricChrgOutCur1 | 04（read） | 3506 | AC-DC Charging module - the DC output current | A | 100
B4 | Grid charging output power L | UP-ElectricChrgOutPowL1 | 04（read） | 3507 | AC-DC Charging module - the DC output power | W | 100
B5 | Grid charging output power H | UP-ElectricChrgOutPowH1 | 04（read） | 3508 |  | W | 100
B6 | Grid total generated energy L | UP-ElectricAggChrgL1 | 04（read） | 350F | Cleared after accumulated overflow | KWH | 100
B7 | Grid total generated energy H | UP-ElectricAggChrgH1 | 04（read） | 3510 |  | KWH | 100
B8 | Grid charging device state | UP-ElectricChrgSta1 | 04（read） | 3511 | D15-D14: 00H Input voltage normal, 01H Input voltage low, 02H Input voltage high, D13～D12,output power.00-lowload，01-middle，02-rated，03-overload D11: Short circuit D9: Over temp. D8: Output voltage abnormal D1: 0 Normal，1 error |  | 1
B9 | Grid charging device temp. | UP-ElectricChrgTemp1 | 04（read） | 3512 | Grid charging device measures the temperature obtained by own sensor | ℃ | 100
B10 | Array input voltage | UP-PvInVolt1 | 04（read） | 3519 | Photovoltaic cell array terminal voltage | V | 100
B11 | Array input current | UP-PvInCur1 | 04（read） | 351A | Photovoltaic cell array terminal current | A | 100
B12 | Array input power L | UP-PvInPowL1 | 04（read） | 351B | Photovoltaic cell array terminal power L | W | 100
B13 | Array input power H | UP-PvInPowH1 | 04（read） | 351C | Photovoltaic cell array terminal power H | W | 100
B14 | Array output voltage | UP-PvOutVolt1 | 04（read） | 351D | Usually refers to the output voltage of the battery terminal | V | 100
B15 | Array output current | UP-PvOutCur1 | 04（read） | 351E | Usually refers to the output current of the battery terminal | A | 100
B16 | Array output power L | UP-PvOutPowL1 | 04（read） | 351F | Usually refers to the output power of the battery end (L) | W | 100
B17 | Array output power H | UP-PvOutPowH1 | 04（read） | 3520 | Usually refers to the output power of the battery end (H) | W | 100
B18 | Array total generated energy L | UP-PvAggChrgL1 | 04（read） | 3527 | Photovoltaic battery array cumulative charge account (L) | KWH | 100
B19 | Array total generated energy H | UP-PvAggChrgH1 | 04（read） | 3528 | Photovoltaic battery array cumulative charge account (H) | KWH | 100
B20 | Array charging device state | UP-PvChrgStat1 | 04（read） | 3529 | D15～D14 Input voltage state。00 Input voltage normal，01 no access 02H Input voltage high，03H Input voltage error D13: Charging MOSFET is short circuit. D12: Charging or Anti-reverse MOSFET is open circuit. D11: Anti-reverse MOSFET is short circuit. D10: Input is over current. D1: 0 Normal，1 error D3～D2charging state 00H No charging,01H Float,02H Boost, 03H Equalization The state of cut-in or cut-out determines whether to cut-in or cut-out according to the input power of the array. (0 is cut-out) |  | 1
B21 | Array charging device temp. |  | 04（read） | 352C | The device measures the sampling temperature of the power device heat sink through own sensor | ℃ | 100
B22 | Inverter input voltage | UP-InverterInVolt | 04（read） | 352F | DC-AC Discharge module - current voltage at the input side | V | 100
B23 | Inverter output voltage | UP-InverterOutVolt | 04（read） | 3533 | DC-AC Discharge module - current voltage at the output side | V | 100
B24 | Inverter output current | UP-InverterOutCur | 04（read） | 3534 | DC-AC Discharge module - current current at the output side | A | 100
B25 | Inverter output state | UP-InverterOutSta | 04（read） | 3535 | D15-D14: 00H Input voltage normal, 01H Input voltage low, 02H Input voltage high, D13～D12,output power.00-lowload，01-middle，02-rated，03-overload D11: Short circuit D9: Over temp. D8: Output voltage abnormal D1: 0 Normal，1 error Switching state judges whether to turn on or off according to the actual voltage of the Inverter output |  | 1
B26 | Inverter output apparent power L | UP-InverterOutApparentPowL | 04（read） | 3536 | Inverter output apparent power | W | 100
B27 | Inverter output apparent power H | UP-InverterOutApparentPowH | 04（read） | 3537 |  | W | 100
B28 | Inverter output frequency | UP-InverterOutFrq | 04（read） | 353B | DC-AC current frequency at the output side | HZ | 100
B29 | Battery voltage | UP-BattVolt | 04（read） | 354C | System current battery voltage | V | 100
B30 | Battery temp. | UP-BattTemp | 04（read） | 354F | The battery temperature measured by the device through own sensor | ℃ | 100
B31 | Battery capacity | UP-BatSOC | 04（read） | 3550 | Percentage of remaining battery power | AH | 1
B32 | Battery state | UP-BattStat | 04（read） | 3553 | D3-D0: 00H Normal ,01H Over Voltage. , 02H Under Voltage, 03H Over discharge, 04H Fault D7-D4: 00H Normal, 01H Over Temp.(Higher than the warning settings), 02H Low Temp.(Lower than the warning settings) D8: Battery inner resistance abnormal 1,normal 0 D15: 1-Wrong identification for rated voltage |  | 1
B33 | Bypass voltage | UP-ByPassVolt | 04（read） | 3558 | Inverter bypass voltage | V | 100
B34 | Bypass current | UP-ByPassCur | 04（read） | 3559 | Inverter bypass current | A | 100
B35 | Bypass power L | UP-ByPassPowL | 04（read） | 355A | Inverter bypass power | W | 100
B36 | Bypass power H | UP-ByPassPowH | 04（read） | 355B |  | W | 100
Number | Variable name | Program variable name | Function code(hex) | Address | Description | Unit | Times
Setting parameter（read or write）0x9600-96FF
C1 | Backlight time | UP-SysBackLightDelaySec | 03（read）10（write） | 9600 | LCD backlight illumination delays the number of seconds after this setting is turned off | S | 100
C2 | Buzzer alarm | UP-SysBuzzerAlarmDelaySec | 03（read）10（write） | 9601 | Buzzer alarm time, 0 means no work, 1 means alarm. |  | 1
C3 | Temp. unit | UP-SysTempUnit | 03（read）10（write） | 9602 | 0001H degrees Celsius, 0000H Fahrenheit |  | 1
C4 | Dry contact on battery voltage | UP-SysDryOnVolt | 03（read）10（write） | 9603 | 43.2-48.0V，According to the battery voltage, the dry contact is closed below this value. | V | 100
C5 | Dry contact off battery voltage | UP-SysDryOffVolt | 03（read）10（write） | 9604 | 48.0V-53.0V，According to the battery voltage, the dry contact is disconnected above this value.（53.0V） | V | 100
C6 | Stop subCharging module charging voltage | UP-SysStopSubChrgVolt | 03（read）10（write） | 9605 | When the battery voltage is higher than this value, the auxiliary charging module stops charging (in the mains priority case, the battery voltage is higher than this value, the solar auxiliary charging is turned off; or the PV voltage is higher than this value, the mains auxiliary charging is turned off) | V | 100
C7 | Restart subCharging module charging voltage | UP-SysRecSubChrgVolt | 03（read）10（write） | 9606 | Battery voltage is lower than this value, the auxiliary charging module starts charging (in the mains priority, the battery voltage is lower than this value, the solar auxiliary charging is turned on; or the PV priority is lower, the battery voltage is lower than this value, the mains auxiliary charging is turned on) | V | 100
C8 | Battery type | f | 03（read）10（write） | 9607 | 0001H Sealed, 0002H GEL, 0003H Flooded, 0004H LiFePO4 battery, 0005H MnNiCo ternary battery , 0000H, User, user defined |  | 1
C9 | Battery capacity | UP-SysBattCap | 03（read）10（write） | 9608 | The nominal capacity of the battery (group) used in the system | AH | 1
C10 | System charging boost hold time | UP-SysChrgBoostHoldTime | 03（read）10（write） | 960B | The cumulative number of minutes that the battery is continuously maintained above the boost voltage. Usually 60-120 minutes. The cumulative process is set to a time length of 1.5 times the value. | Minute | 1
C11 | System charging boost voltage | UP-SysChrgVCtrl_BCV | 03（read）10（write） | 960D | When the battery (group) terminal voltage is lower than the boost recovery voltage, a constant voltage current-limiting charging voltage is used to ensure the battery (group) is full, which is called a boost voltage. The charging is generally 1 to 3 hours, usually 2 hours. After the lifting is completed, it should be transferred to the floating charging stage. | V | 100
C12 | System charging float voltage | UP-SysChrgVCtrl_FCV | 03（read）10（write） | 960E | After the battery (group) completes the equalization or boost charging phase, it enters the floating charging phase, at which time the battery (group) target voltage maintained by the controller is the floating charging voltage, and the battery (group) is always maintained at the voltage. | V | 100
C13 | System charging boost recovery voltage | UP-SysChrgVCtrl_BCV | 03（read）10（write） | 960F | System charging boost recovery voltage | V | 100
C14 | Charging priority mode | UP-ChrgPriorityMode | 03（read）10（write） | 9616 | Four charging modes 2 solar priority charging mode 4 grid and solar charging mode 8 solar charging mode only 1 grid priority charging mode |  | 1
C15 | Total charging current | UP-SysAggChrgCur | 03（read）10（write） | 9617 | Grid charging current + solar charging current, this current is the sum of grid and PV current, the actual charging current can not exceed this set value | A | 100
C16 | DC-AC module low voltage disconnection voltage | UP-DcAc_LVD | 03（read）10（write） | 9621 | In order to prevent the battery (group) from being over-discharged and ensuring that it has a certain residual capacity (generally 10-40%), the battery (group) terminal voltage of 20% of the remaining capacity is usually taken as the low-voltage disconnection voltage. When the battery (group) terminal voltage drops to the set value, the all-in-one disconnects the load output. | V | 100
C17 | DC-AC module low voltage disconnection recovery voltage | UP-DcAc_LVR | 03（read）10（write） | 9622 | When the battery (group) terminal voltage is higher than the voltage, the low-voltage disconnection action is eliminated, and the load output is restored. This voltage value is the low voltage disconnect recovery voltage. | V | 100
C18 | DC-AC module overvoltage disconnection recovery voltage | UP-DcAc_OVR | 03（read）10（write） | 9623 | Calculated based on other quantities. The measured battery voltage is lower than the discharge and charging of this voltage recovery system. | V | 100
C19 | DC-AC module overvoltage disconnection voltage | UP-DcAc_OVD | 03（read）10（write） | 9624 | The measured battery voltage exceeds this voltage to turn off the system's discharge and charge | V | 100
Number | Variable name | Program variable name | Function code(hex) | Address | Description
Switch
D1 | Clear generated statistics | UP-bClrStat | 01(read)05（write） | 0100 | 0-1（0 unable，1 able）
D2 | clear error | UP-bClrErrors | 01(read)05（write） | 0101 | 0-1（0 OFF，1 ON）
D3 | Output priority mode | UP-bOutPriorMode | 01(read)05（write） | 0104 | 0 Battery priority power supply mode (inverter priority) 1 Grid bypass priority power supply mode (grid priority)
D4 | Inverter output energy-saving mode | UP-bOutPriorMode | 01(read)05（write） | 0105 | 1 enter power-saving mode 0 exit power-saving mode
D5 | Load output switch | UP-bDevOutOnOff | 01(read)05（write） | 0106 | 1 Inverter turns on 0 Inverter turns off
D6 | Local/Remote control | UP-bLocalRemoteCtrl | 01(read)05（write） | 0108 | 1 Remote 0 Local（Default local switch and power-saving mode enable after power off）
D7 | System reset switch | UP-bSysResetOnOff | 01(read)05（write） | 010A | 0 no reset，1reset
D8 | PV charging switch | UP-bPvChrgOnOff | 01(read)05（write） | 010B | 1 controller open charging 0 controller close charging
D9 | Grid charging switch | UP-bGridSupplyChrgOnOff | 01(read)05（write） | 010C | 1 ACDC open charging 0 ACDC close charging
Discrete
E1 | Inverter bypass | UP-bByPassSta | 02（read） | 2100 | 1-grid，0-no grid（Inverter whether has grid）
E2 | Day/Night | UP-bNight | 02（read） | 2101 | 0-Night，1-Day